## Panel Data Sheet
Sec 1 | Panel Name: | Notes/Examples | Sample Panel Entry
| Date Updated: |  | 2021-02-15
Section 2 Location | Building Number: |  | 512
| UF Stars Room Number: |  | 105
| Location in Room: |  | North Wall
Section 3 General | Panel Manufacturer: | Square D, Siemens, Eaton, GE | Square D
| Panel Model: | NQ, NF, QED, HCM, Spectra, A-Series | NF
| Date of Manufacture: | must enter in format MO/DY/YEAR | MM/DD/YYYY
| Rated Voltage: | 480/277 or 208/120 | 480/277
| Mount: | Surface/Flush | Surface
| Main Breaker Size (Amps): | Main breaker amperage rating (If MLO write MLO and see Feeder Breaker below) | 75 Amps
| Phase: | 1 or 3 | 3
| Bus Rating (Amps) |  | 225
| Qty of Poles or Circuits Total: | total qty of poles | 42
| Qty of Poles or Circuits Used (ON): | Not including spares | 18
| TVSS or SPD | yes or no | yes
| Integral Power Meter | yes or no | no
| Type of power: | Normal/Life Safety/Optional Standby/UPS | Normal
| kAIC: | 10,14,22,25,42,65 | 42
| Arc Flash: | calculated cal/cm2
Section 4 Feeder & Circuits | Feed From Panel Name: | Required | 4MDS
| Feeder Breaker size | Required if MLO Panel (or if Main is larger then Feeder Breaker) | 75 Amps
| Feed From Panel Stars Room Number: | Required | 106
Section 5 Initial Investigation | Voltage A to B Phase | Data From Load Check
Voltage A to C Phase
Voltage C to B Phase
Voltage Neutral to A Phase
Voltage Neutral to B Phase
Voltage Neutral to C Phase
Current Load A Phase
Current Load B Phase
Current Load C Phase
Current Load Neutral
Section 6 Proposed Load | Proposed additional (or Removed) Load A Phase | Amps
| Proposed additional (or Removed) Load B Phase | Amps
| Proposed additional (or Removed) Load C Phase | Amps
Section 7 Load Study | Load Study Date |  | MM/DD/YYYY
| Duration of Load Study | 3 - 30 days
| Max Load on L1 | metered peak
| Max Load on L2 | metered peak
| Max Load on L3 | metered peak
| Average Load on L1 | metered average
| Average Load on L2 | metered average
| Average Load on L3 | metered average
Section 8 Total Expected Load | Expected or Anticipated new load A Phase | Current Load (from Load check, 3 day or 30 day load study) plus the section 7 (the added or removed load)
Expected or Anticipated new load B Phase
Expected or Anticipated new load C Phase

## Panel Schedule
Contractor Name:
Contractor Contact:
Project Number: |  |  |  |  | Project Date:
Panel Name: |  |  |  |  | Panel Fed From (# and Room #):
Panel Voltage: |  |  |  |  | Panel kAIC:
Panel Ampacity: |  |  |  |  | Panel Arc Flash Rating:
Panel Schedule
Project | Date | Desription | Circuit | Circuit | Description | Date | Project
|  |  | 1 | 2
|  |  | 3 | 4
|  |  | 5 | 6
|  |  | 7 | 8
|  |  | 9 | 10
|  |  | 11 | 12
|  |  | 13 | 14
|  |  | 15 | 16
|  |  | 17 | 18
|  |  | 19 | 20
|  |  | 21 | 22
|  |  | 23 | 24
|  |  | 25 | 26
|  |  | 27 | 28
|  |  | 29 | 30
|  |  | 31 | 32
|  |  | 33 | 34
|  |  | 35 | 36
|  |  | 37 | 38
|  |  | 39 | 40
|  |  | 41 | 42

## 3-Day Load Study
3 Day Load Study Ledger
Panel:
Start Date:
| Time | Phase 1 Amp. | Phase 2 Amp. | Phase 3 Amp.
Day 1 | 800
1100
1400
1600
Day 2 | 800
1100
1400
1600
Day 3 | 800
1100
1400
1600