## Rebate Areas
Instructions: Below fill in the Project and Contact Information completely. Next, mark an "X" for each potential rebate the project may be eligible for. Grayed out boxes indicate ineligible programs for participation. For each requested rebate, please either click the hyperlink to the right or visit the respective tab at the bottom of this spreadsheet. Once all the required documentation has been gathered, please contact Dustin Stephany for processing.
Duke Energy Rebate Program
Project Information
Project # and Name
UF Building Name and Number
Project SF |  |  | Square Feet
Contact Information
UF Project Manager
Item | Retrofit | New Construction | Incentive Requirements | Responsible Party
Ceiling Insulation Upgrade |  |  | Ceiling Insulation Upgrade | PDC
Roof Insulation Upgrade |  |  | Roof Insulation Upgrade | PDC
Cool Roof |  |  | Cool Roof | PDC
Demand Control Ventilation |  |  | Demand Control Ventilation | PDC
High Efficiency Energy Recovery Ventilation (ERV) |  |  | Energy Recovery Ventilation | PDC
High Efficiency Chillers |  |  | High Efficiency Chillers | PDC
Small Heat Pumps (<65,000Btu/h) |  |  | Small Heat Pumps | PDC
Single Package Vertical Units, Unitary AC Units & Heat Pumps (>65,000 Btu/h) |  |  | Unitary AC Units and Heat Pumps | PDC
PTHPs & PTACs |  |  | PTHPs and PTACs | PDC
PTAC/PTHP Coil Cleaning |  |  | Coil Cleaning | FS
Duct Check and Repair Program |  |  | Duct Check and Repair Program | FS
Chiller Tuneup |  |  | Chiller Tuneup | FS
HVAC Tuneup |  |  | HVAC Tuneup | FS
Rooftop HVAC Recommissioning |  |  | Rooftop HVAC Recommissioning | FS
Florida Custom |  |  | Custom Incentives | PDC
General Disclaimer In the event of an omission of Customer Requirements or Required Documents, Progress Energy Better Business (Retrofit) & New Construction Program documents supersede all items found in this Rebate Checklist

## Ceiling
Ceiling Insulation Upgrade | [6 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Eligible facilities must have central electric air conditioning and central electric heating (non-portable). |  | 1 |  | Invoices from contractor indicating system/material costs
2 | Facilities with dropped acoustic tile ceilings do not qualify. |  | 3 |  | Substantial Completion or Certificate of Occupancy form |  |  |  | Example
3 | Flat roofs must have space to allow a minimum of three inches of air space above new insulation. |  | 6 |  | FINAL R-Value of Upgraded Insulation
4 | Insulation must have a minimum clearance (meeting state, county and local codes) around all recessed lighting and gas-fired appliances. |  | 7 |  | Floor plan with Ceiling Area (SF) |  |  |  | Example
5 | Radiant barriers are not allowed as a substitute for insulation. |  | 8 |  | Contractors Submittal (specs/datasheets) |  |  |  | Example
6 | Commercial multifamily units will be qualified as individual units for incentive purposes. |  | Ceiling Insulation
7 | Insulatoin must have a minimum value of either R-19 or R-38 and be uniformly installed.
8 | Building must be at least two years old at the time of the audit.
9 | The weighted average R-value of the existing insulation above the conditioned space must be less than or equal to R-12
10 | Insulation must be over conditoined space; facility must have electronic AC and Unit |  |  | Measure |  | Incentive | Unit
| Rebate Home |  |  | R-19 to R-37 |  | 0.1 | SF
|  |  |  | > R-38 |  | 0.175 | SF
Rebate Calculation Assistance
| Please indicate the R-Value of the Ceiling insulation | R-
| Please enter the total SF of celing area |  | SF
Total Potential Rebate

## Roof Ins
Roof Insulation Upgrade | [5 empty] | Updated: | 2016-10-27
Customer Requirements |  |  |  | Required Documents for Submission Checklist
1 | The insulation must be installed per the manufacturer’s recommendations and specifications. |  | 1 |  | Invoices from contractor indicating roof system/material costs
2 | The insulation must be installed in the roof deck assembly. |  | 2 |  | Contractor's submittal and supporting documents |  |  | Example
3 | The insulation must be installed uniformly, resulting in a minimum R-19 for retrofit projects and greater than R-38 for new construction. |  | 3 |  | Media Inches |  |  | Example
4 | The weighted average R-value of the existing insulation under the total roof square footage (above the conditioned space) must be less than R-12. |  | 4 |  | Roof plan with Area (SF) |  |  | Example
5 | Eligible facilities must have whole-facility electric air conditioning and whole-facility electric heating (nonportable). |  | 5 |  | R-Value (Final) |  |  | Example
6 | Maximum incentive payout is $50,000 per Building |  | 6 |  | Certificate of Occupancy form |  |  | Example
7 |  |  | 7
| Rebate Home |  | 8
Roof Insulation Upgrade
| Rebate Calculation Assistance |  |  |  | Measure |  | Incentive | Unit
| Is this project considered new construction or a renovation? |  |  |  | New Construction R-38 |  | 0.07 | Per SF
| What is the R-Value of the Roof insulation? | R- |  |  | Retrofit R-19 |  | 0.07 | Per SF | New Construction
| What is the area of the roof? | [7 empty] | Retrofit
| If sloped please include actual area not floor area covered |  | SF
| Potential Rebate | No Rebate

## Cool Roof
Cool Roof | [6 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Earn $0.15/square foot of roof, with a maximum incentive of $50,000 per building. |  | 1 |  | Invoices from contractor indicating system/material costs
2 | Initial solar reflectance must be greater than or equal to 0.76, which means the cool roof is reflecting 76 percent of the solar radiation. |  | 2 |  | Roof plan with Area (SF) |  |  |  | Example
3 | ENERGY STAR® labeled roof product based on ASTM E-903 or ASTM C-1549 testing. |  | 3 |  | Substantial Completion or Certificate of Occupancy form |  |  |  | Example
4 | Applied by a licensed contractor. |  | 4 |  | Contractor submittals (specs) |  |  |  | Example
5 | Cool Roof must be flat and over conditioned space. |  | Cool Roof
6 | Cooling system must be all electric
Resources
1 | Cool Roof Rating Council |  |  | Measure |  | Incentive | Unit
|  |  |  | SR 76 |  | 0.15 | SF
Rebate Home
Rebate Calculation Assistance
| Please indicate the Initial Solar Reflectance value for the roofing material | Initial Solar Reflectance
| Please enter the total SF of roof area |  | SF
| Total Potential Rebate | No Rebate

## DCV
Demand Control Ventilation | [6 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | HVAC equipment must be electric |  | 1 |  | Invoices for products/services supporitng DCV (CO2 sensors, wiring, engineering & design, M&V, etc.) |  |  |  | Example
2 | Customer must provide an engineering report documenting DCV system and projected HVAC tonnage reduction. |  | 2 |  | Contractor's Submittal with system size (tons) and performance |  |  |  | Example
3 | DCV installation must include CO2 measuring sensors that adjust ventilation rate based on varying occupancy by integrating CO2 sensor readings to control outside air dampers. Other ventilation rate control methods are accepted. |  | 3 |  | Engineering report documenting DCV system and projected HVAC tonnage reduction. |  |  |  | Example
4 | Sensors should be placed in locations so they are not accessible by building occupants |  | 4
5 | The incentive rebate will not exceed 50% of the total HVAC project or service cost |  | 5
6 |  |  | Demand Control Ventilation
7 | Rebate Home
Rebate Calculation Assistance
| Please indicate the tonnage reduction controlled by the CO2 sensors |  |  | Measure |  | Incentive | Unit
| Potential Rebate | 0 |  | no electric heat |  | 50 | ton
|  |  |  | electric heat |  | 50 | ton

## ERV
High Efficiency ERV | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Confirm ERV unit ARI 1060 rating is greater than 65 percent winter effectiveness @ 100% air flow. |  | 1 |  | Invoices contractor indicating system/material costs
2 | ERV must be a minimum of 450 CFM per unit. |  | 2 |  | Contractor submittals with AHRI 1060 Rating (SCFM), Winter effectiveness (%) |  |  | Example
3 | Equipment must be listed by Underwriters Laboratories (or other nationally recognized testing laboratories in accordance with UL standards). |  | 3 |  | Quantities
4 | Equipment efficiency ratings from Air Conditioning, Heating, and Refrigeration Institute (AHRI) should meet or exceed rating procedure standard 1060-2000. |  | High Efficiency Energy Recovery Ventilation
5 | System must have electric cooling and heating
6
Rebate Home
| Rebate Calculation Assistance |  |  | Measure |  | Incentive | Unit
| Please identify the size of the ERV measured in CFM |  |  | No electric heat |  | 1.4 | Per CFM
| Potential Rebate | no rebate |  | With electric heat |  | 1.4 | Per CFM

## Chillers
High Efficiency Chillers | [5 empty] | Updated: | 2016-10-27
Customer Requirements |  |  |  | Required Documents for Submission Checklist |  |  |  |  | EEB Incentive Eligibility Requirements
1 | Chiller efficiencies and performance specifications should be calculated at Air Conditioning, Heating, and Refrigeration Institute (AHRI) test conditions (550/590 Test Standards.) |  | 1 |  | Invoice(s) for unit costs |  |  |  | AIR COOLED AND WATER COOLED ELECTRIC CHILLERS (AHRI 550/590 Test Standards)
2 | For air cooled and water cooled electric chillers, confirm that cooling load calculations are performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency uint is adding cooling to previously unconditioned space. |  | 2 |  | Contractors submittal |  |  | Example | Chiller Type and Size Range | 2010 State Energy Code Standard | Minimum Efficiency Eligible for Incentive
3 | Minimum efficiency can be either FL. Or IPLV. |  | 3 |  | Substantial Completion or Certificate of Operation form |  |  | Example | Water Cooled Centrifugal
[9 empty] | Under 150 tons | FL*: 0.634 kW/ton IPLV**: 0.596 kW/ton | FL: 0.571 kW/ton IPLV: 0.405 kW/ton
| Rebate Home |  | High Efficiency Chillers | [5 empty] | 150-300 tons | FL: 0.634 kW/ton IPLV: 0.596 kW/ton | FL: 0.571 kW/ton IPLV: 0.405 kW/ton
[9 empty] | 300-600 tons | FL: 0.576 kW/ton IPLV: 0.549 kW/ton | FL: 0.513 kW/ton IPLV: 0.360 kW/ton
[9 empty] | Over 600 tons | FL: 0.570 kW/ton IPLV: 0.539 kW/ton | FL: 0.513 kW/ton IPLV: 0.360 kW/ton
Water Cooled Positive Displacement
| Rebate Calculation Assistance |  |  |  | Measure |  | Incentive | Unit | Under 75 tons | FL: 0.780 kW/ton IPLV: 0.630 kW/ton | FL: 0.760 kW/ton IPLV: 0.540 kW/ton
| Please identify the total cooling capacity of the chiller being installed (in tons) |  |  |  | Air and Water cooled |  | 50 | Per ton | 75-150 tons | FL: 0.775 kW/ton IPLV: 0.615 kW/ton | FL: 0.750 kW/ton IPLV: 0.527 kW/ton
| Total Potential Rebate | 0 | [6 empty] | 150-300 tons | FL: 0.680 kW/ton IPLV: 0.580 kW/ton | FL: 0.660 kW/ton IPLV: 0.486 kW/ton
[9 empty] | Over 300 tons | FL: 0.620 kW/ton IPLV: 0.540 kW/ton | FL: 0.610 kW/ton IPLV: 0.441 kW/ton
Air Cooled
[9 empty] | Any Size | FL: 9.562 EER IPLV: 12.50 EER | FL: 10.16 EER IPLV: 13.75 EER
*Full Load
**Integrated Part Load Value

## Small HP
Small Heat Pump (<65,000Btu/h or 5.5 tons) | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
* | Replacing Resistance Heat: Required cooling efficiency of 15 SEER and a minimum heating efficiency of 8.2 HSPF |  | 1 |  | Invoices from the contractor indicating system/material costs
* | Replacing Heat Pump: Required cooling efficiency of 15 SEER and a minimum heating efficiency of 8.2 HSPF |  | 2 |  | Unit Quantities
* | If the capacity of the high-efficiency unit differs from that of the original unit - or if the high-efficiency unit is adding cooling to previously unconditined space - then cooling and heating load calculations nust also be performed |  | 3 |  | Contractor submittals |  |  | Exanple
1 | Heat pump must be all electric |  | Small Heat Pump
2 | All equipment must be new and not refurbished, previously installed, or used
3
4 | Rebate Home
| Rebate Calculation Assistance |  |  |  | Measure |  | Incentive | Unit
| Please identify the number of small heat pumps to be replaced |  |  |  | Replacing heat pump |  | 200 | per system
| Do these heat pumps have heat resistance? |  |  |  | Replacing resistance heat |  | 375 | per system
| Potential Rebate | 0 | [6 empty] | Yes
No
Maybe

## Unitary
Unitary Air Handler Unit and Heat Pumps (> 65,000 Btu/h) | [6 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Ensure all equipment meets Air Conditioning, Heating, and Refrigeration Institute (AHRI) certification efficeency data at Standard Rating Conditions (AHRI 210/240-94 for units <135,000 Btu/h and 340/360 for units > 135,000 Btu/h) |  | 1 |  | Invoices from the contractor indicating system/material costs
2 | Confirm that cooling and heating load calculation are performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency unit is adding cooling or heating to previously unconditioned space. |  | 2 |  | Contractor submittals |  |  |  | Example
3 | Single Package Vertical Units Also qualify for this rebate |  | 3 |  | AHU Quantities
| Rebate Home |  | Unitary AC Units & Heat Pumps (>65,000
| Rebate Calculation Assistance |  |  | Measure |  |  | Incentive | Unit
| Please identify the number of AHU units associated to the project | 1 |  | Large AC Units |  |  | 75 | Per ton
| Please identify the unit of measurement | MBTU/H |  | Large Heat Pumps |  |  | 75 | Per ton
Please enter the cooling capacity of each AHU (found on Mech plans)
| AHU 1 | 175 | MBTU/H |  | 145.25 | tons | 10893.75 |  |  | MBH
[5 empty] | 0 |  |  |  |  | MBTU/H
[5 empty] | 0 |  |  |  |  | BTU/H
|  |  | " |  | 0 |  |  |  |  | Tons
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[6 empty] | Total Potential Rebate | 10893.75

## PTAC
Packaged Terminal Heat Pumps (PTHPs) & Packaged Terminal Air Conditioners (PTACs) | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Provide an itemized inventory of equipment installed and Air Conditioning, Heating, and Refrigeration Institute (AHRI) certification data at Standard Rating Conditions (AHRI 310/380) |  | 1 |  | Invoices of material costs
2 | Cooling load calculations msut be performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency unit is adding cooling to previously unconditioned space. |  | 2 |  | Contractor's submittal
3 |  |  | PTHPs and PTACs
4
Rebate Home
|  |  |  | Measure |  | Incentive | Unit
| Rebate Calculation Assistance |  |  | PTACs replacing less efficent PTAC |  | 100 | Per ton
| Please indicate the total number of PTHPs and/or PTACs |  |  | PTHP replacing PTACs |  | 100 | Per ton
Please indicate the total cooling capacity of each unit (tons)
| Potential Rebate | 0

## Coil
Coil Cleaning | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Ensure the cleaning process to be used is preapproved by a Duke energy inspector. |  | 1 |  | Invoices from a licensed contractor indicating system/material costs and an inventory of equipment cleaned.
2 | Inform Duke Energy of the cleaning date to allow for random inspections of the cleaning process. |  | 2
3 | All qualifying HVAC equipment are eligible for a one-time coil cleaning incentive over their lifetime. |  | 3
4 | The maximum incentive payout cannot exceed 50% of the total project or service cost. |  | 4
5 |  |  | 5
6 | Rebate Home |  | 6
Coil Cleaning
| Rebate Calculation Assistance |  |  |  | Measure |  | Incentive | Unit
| Please indicate the number of PTAC/PTHP units |  | Units |  | PTAC/PTHP |  | 20 | Per unit
| OR |  |  |  | AHU/RTU |  | 20 | per ton
Please indicate the number of AHU/RTU with coils cleaned
Please indciate the tonnage of each AHU or RTU
| Total Potential Rebate | 0

## Duct
Duct Check and Repair Program | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Duct test and repairs are for businesses with centrally ducted electric heating and cooling systems. |  | 1 |  | Invoices from contractor indicating system/QTY/material costs
2 | HVAC systems must be 5.5 tons or less (65,000 BTUs). |  | 2 |  | Contractor submit Duct Check form |  |  | Example
3 | Duct check procedures must be completed by a DEF approved contractor*. |  | 3
4 | In commercial multifamily units, if the contractor seals all joints and connections of the duct work, no duct test is required. |  | 4
5 | Multifamiliy units greater than one story in height can only have the top floor duct system(s) repaired or sealed due to safety concerns. |  | 5
6 | Commercial multifamily units will be qualified as individual units for incentive purposes. |  | Duct Check Program
* | DEF Approved Contractors
Rebate Home
| Rebate Calculation Assistance |  |  | Measure |  |  | Incentive | Unit
| Please identify the number of duct units tested |  |  | Duct Test (1st Unit) |  |  | 30 | AHU Unit
| Rebate from duct testing | 0 |  | Duct Test (additional) |  |  | 20 | AHU Unit | Yes
| Do the duct units repaired have electrical heat installed in it? |  |  | Duct Repair non ducted electrical heat |  |  | 25% repair | AHU Unit | No
| Please identify the repair costs for repairing ducts |  |  | Duct Repair ducted electrical heat |  |  | 50% repair | AHU Unit | Maybe
| Rebate from fixing duct work | 0
| Total Potential Rebates | 0

## Chlr Tune
Chiller Tuneup | [5 empty] | Updated: | 2016-10-27
Customer Requirements |  |  |  | Required Documents for Submission Checklist
1 | Ensure that all equipment tuneups and repairs meet manufacturer's instructions and specifications. |  | 1 |  | Invoices from contractor indicating system tuneup/material costs/repair costs
2 | This incentive is available only once over the life of the chiller. |  | 2 |  | Contractor submit Chiller Tuneup Form |  |  | Example
3 | This incentive is capped at a maximum of 50 percent of the total project cost. |  | 3
4 | Rebate Home |  | 4
5 |  |  | Chiller Tuneup
| Rebate Calculation Assistance |  |  | Measure |  | Incentive | Unit
| Please indicate the total cost to repair/tuneup the chiller |  |  | Chiller Tune Up |  | 5 | Per ton
Please indicate the total cooling capacity of the chiller (in tons)
| Potential Rebate | 0

## HVAC Tune
HVAC Tuneup | [5 empty] | Updated: | 2016-10-27
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
1 | Ensure that all equipment tuneups and repairs meet manufacturer's instructions and specifications. |  | 1 |  | Invoices from contractor indicating system tuneup/material costs/repair costs
2 | This incentive is available only once over the life of the HVAC unit. |  | 2 |  | Contractor submit HVAC Tuneup Form |  |  | Example
3 | This incentive is capped at a maximum of 50 percent of the total project cost. |  | 3
4 |  |  | HVAC Tuneup
5
6
| Rebate Home |  |  |  | Measure |  | Incentive | Unit
[5 empty] | Strait Cool |  | 25 | Per ton
[5 empty] | Heat Pump |  | 25 | Per ton
Rebate Calculation Assistance
Please indicate the number of units being tuned up
Please indciate the tonnage of each unit
| Total Potential Rebate | 0

## Roof HVAC
Rooftop HVAC Recommissioning | [5 empty] | Updated: | 2016-10-27
Customer Requirements |  |  |  | Required Documents for Submission Checklist
1 | Confirm that all equipment tuneups and repairs must meet manufacturers’ instructions and specifications. |  | 1 |  | Invoice from contractor with system/repair costs
2 | Rooftop HVAC recommissioning is a one-time incentive. |  | 2 |  | Contractor submit recommissioning form |  |  | Example
3 | Incentive is capped at a maximum of 50 percent of the total project cost. |  | 3
4 |  |  | 4
| Rebate Home |  | Rooftop HVAC Recommissioning
| Rebate Calculation Assistance |  |  |  | Measure |  | Incentive | Unit
| Please indicate the number of Rooftop Units being Recommissioned |  |  |  | Strait Cool |  | 25 | Per ton
| Please indciate the tonnage of each unit |  |  |  | Heat Pump |  | 25 | Per ton
| Total Potential Rebate | 0

## FL Custom
Florida Custom Program |  |  |  |  | Updated: | 2016-10-27
Customer Qualifications |  |  | Required Documents for Submission Checklist
| The objective of the Florida Custom Program is to encourage customers to make capital investments for the installation of energy efficiency measures which reduce peak kW demand and/or kWh energy on the DEF system. Energy efficiency and peak demand deferrals are the result. Eligible projects include, but are not limited to, new technologies, which emerge from national, State and local sources that have proven to be cost-effective and are not otherwise addressed by DEF programs. Each project will be evaluated for cost-effectiveness based on its demand and energy effects to determine the applicable RIM-based incentive. | 1 |  | Submit a Florida Custom Program Pre-Application Questionaire |  |  | Questionaire
| Custom Incentives | 2 |  | Invoices or an email from contractor indicating the cost of the system/material
| Rebate Home | 3 |  | Certificate of Occupancy form |  |  | Example
Custom Incentives
Measure
Contact PDC Sustainable Building Coordinator

## Overview
|  |  | Substantial Completion Form | Product Submittals | Product Invoices | Documented R-Value | Floor Plan w/ Conditioned Area Calculation | Tonnage Reduction Calculations | Total Tonnage Cleaned | Submit Duke Energy Form
Rebate Type |  |  | Documentation needed
University of Florida Planning, Design & Construction | Ceiling Insulation Upgrade |  | X |  | X | X | X
No drop ceilings, flat roof w/3" air gap, upgrade R-value from <R-12 to R-19 (existing>=2yrs) or R-38 (new)
| Roof Insulation Upgrade |  | X | X | X | X | X
R-19 (retrofit), R-38 (new)
| Cool Roof |  | X |  | X |  | X
Initial Solar Reflectance ≥0.76, Roofing material to be Energy Star labeled or CRRC certified
| Demand Control Ventilation |  |  | X | X |  |  | X
CO2 sensor adjusts ventilation OA dampers, sensor location should not be accessible by building occupant
| High Efficiency Energy Recovery Ventilation (ERV) |  |  | X | X
65% Winter Effectiveness @100% airflow, minimum of 450cfm
| High Efficiency Chillers |  | X | X | X
Air Cooled Chillers to have ≥10.7 EER or IPLV ≥14.95
| Small Heat Pumps (<65,000Btu/h) |  |  | X | X
Heat Pump or Resistance Heat (Cooling efficiency of SEER≥15 and heating efficiency ≥8.2 HSPF)
| Single Package Vertical Units, Unitary AC Units & Heat Pumps (>65,000 Btu/h) |  |  | X | X
Efficiencies are based on size of unit. Please confirm with Duke Energy Representative
| PTHPs & PTACs |  |  | X | X
Units to obtain an Air Conditioning, Heating, and Refrigeration Insitute (AHRI) Certification
University of Florida Facilities Services | PTAC/PTHP Coil Cleaning |  |  |  | X |  |  |  | X
One-time rebate for the life of the unit
| Duct Check and Repair Program |  |  |  | X
Unit to be 5.5tons or less, more rebate available if using ducted electric reheat
| Chiller Tuneup |  |  |  | X |  |  |  |  | X
Repair/tuneup to manufactuers specs, one-time rebate for life of unit
| HVAC Tuneup |  |  |  | X |  |  |  | X | X
Repair/tuneup to manufactuers specs, one-time rebate for life of unit
| Rooftop HVAC Recommissioning |  |  |  | X |  |  |  |  | X
Repair/tuneup to manufactuers specs, one-time rebate for life of unit