## Tech Reqmts
CSI Div. | Item | UF D&C Std. | Training | Training Video'd? | Documentation Requirements IO&M = Installation, Operation, Maintenance PD = product data | Other Documentation Requirements | Attic Stock | Spare Parts
2 | Lift stations | 02700 | YES |  | IO&M and PD documents for lift station, pump, control panel, and float switch
2 | Meters & Gauges | 02660, 02810 |  |  | IO&M and PD documents for irrigation or reclaimed water meters | Meter data sheets
2 | Fire hydrants | 02600 |  |  | IO&M and PD documents for fire hydrants
2 | Fire protection water system | 02660 |  |  |  | Test reports for fire protection water piping
2 | Potable water system | 02660 |  |  | PD for pipe, fittings, devices | Test reports for potable water piping
|  | 15050 |  |  | IO&M and PD documents for potable water backflow preventers | BFP certificates
|  | 15050 |  |  | IO&M and PD documents for potable water meters | Meter data sheets
2 | Manholes | 02600 |  |  | PD
2 | Landscape irrigation system | 02810 |  |  | IO&M and PD documents for valves, automatic controllers, sprinkler heads/outlets, and (when applicable) meters and backflow preventers | Subcontractor as-builts
2 | Landscaping | 02900 |  |  | Care & maintenance instructions for trees, shrubs, ground covers, and grasses | Nursery certificates for trees, shrubs, ground covers, and grasses
4 | Masonry | 04000 |  |  | PD (including colors) for all masonry items, grouts, mortars, and sealants
Div. 6 | Carpentry, Casework, Millwork, Paneling |  |  |  | Care & maintenance instructions and PD for hardware
7 | Dampproofing, Waterproofing, Fireproofing | 07000 |  |  | PD for all sealants, barriers, water and dampproofing, and EIFS products
7 | Roofing | 07500 |  |  | Care & maintenance instructions and PD for all roofing systems and components | Warranty documents for all roofing systems and products
8 | Doors |  |  |  | Care & maintenance instructions and PD
8 | Rolling / Coiling Doors |  | YES |  | IO&M and PD documents
8 | Door hardware | 08700 |  |  | IO&M and PD documents for all, including closers, exit devices, and automatic openers
8 | Storefront systems | 08500 |  |  | IO&M and PD documents for storefront systems, including door hardware
8 | Curtainwall systems | 08500 |  |  | Care & maintenance instructions and PD
8 | Glazing |  |  |  | Care & maintenance instructions and PD
9 | Carpet | 09000 |  |  | Care & maintenance instructions and PD |  | 10%, each type/style (max. two boxes)
9 | Resilient Tile | 09000 |  |  | Care & maintenance instructions and PD |  | 10%, each type/style (max. two boxes)
9 | Ceramic Tile | 09000 |  |  | Care & maintenance instructions and PD |  | 10%, each type/style (max. two boxes)
9 | Stone Tile | 09000 |  |  | Care & maintenance instructions and PD |  | 10%, each type/style (max. two boxes)
9 | Wood Flooring | 09000 |  |  | Care & maintenance instructions and PD |  | 10%, each type/style (max. two boxes)
9 | Suspended Tile Ceiling Systems | 09000 |  |  | PD |  | 10%, each type/style (max. two boxes)
10 | Visual Display Boards |  |  |  | Care & maintenance instructions and PD
10 | Access Floor |  | YES |  | IO&M and PD documents |  | 5%, minimum two panels
10 | Lockers |  |  |  | IO&M and PD documents for lockers and digital/elec locks
10 | Operable Partitions |  | YES | YES | IO&M and PD documents
10 | Mobile Storage Systems (Compact Shelving) |  | YES | YES | IO&M and PD documents
11 | Laboratory Equipment | 11600 | YES | YES | IO&M and PD documents for fume hoods, lab sinks, safety showers, eye wash stations, storage cabinets
11 | Medical Equipment |  | YES | YES | IO&M and PD documents
11 | Library Equipment |  | YES | YES | IO&M and PD documents
11 | Theater Equipment |  | YES | YES | IO&M and PD documents
11 | Athletic & Recreational Equipment |  | YES | YES | IO&M and PD documents
11 | Kitchen / Food Service Equipment |  | YES | YES | IO&M and PD documents
11 | Motorized Projection Screens |  |  |  | IO&M and PD documents
12 | Lab Casework | 12350 |  |  | IO&M and PD documents
12 | Fixed Seating/Tables | 12700 |  |  | IO&M and PD documents
12 | Window Shades |  | YES | YES | IO&M and PD documents
13 | Cleanroom Architectural Systems |  |  |  | IO&M and PD documents
13 | Cold Storage Rooms | 13038 |  |  | IO&M and PD documents
14 | Elevators | 14200 | 4 hours |  | IO&M and PD documents for elevators and lifts, including complete service manuals and, if applicable, Miprom-HS&ST Reference Guide and fault codes | Two (2) sets of laminated as-built wiring diagrams, block diagram, and diagnostic data Copy of the Certificate of Operation from the State of Florida Division of Elevator Inspections. | Fireman elevator recall key and elevator door key | Diagnostic test devices and service tools as needed
15 | Chilled Water System | 02660 | YES |  | PD for pipe, fittings, devices | Test reports for chilled water piping
|  | 15050 |  |  | IO&M and PD documents plus performance curves (DP versus flow) for chilled water balancing valves
|  | 15500 |  |  | IO&M and PD documents for isolation and shut-off valves
|  | 15750 |  |  | IO&M and PD documents for CW coils
|  | 15950 |  |  | IO&M and PD documents for chilled water meters, including test reports | Meter data sheets
| Heating Hot Water System | 15050 | YES |  | IO&M and PD documents plus performance curves (DP versus flow) for HHW balancing valves | Test reports for HHW piping
|  | 15750 |  |  | IO&M and PD documents for HHW expansion tanks, HHW coils, heat exchangers
[5 empty] | IO&M and PD documents for heating hot water meters, including test reports | Meter data sheets
| Steam and Condensate System | 02600 |  |  | IO&M and PD documents for steam & condensate manholes | Test reports for steam & condensate piping
|  | 15050 |  |  | IO&M and PD documents plus performance curves (DP versus flow) for condenser water balancing valves
|  | 15050 |  |  | IO&M and PD documents for pressure-reducing valves (with valve type clearly indicated)
|  | 15500 |  |  | IO&M and PD documents for isolation and shut-off valves
|  | 15500 |  |  | IO&M and PD documents for pumps and receivers
IO&M and PD documents for heat exchangers
|  | 15750 |  |  | IO&M and PD documents for steam coils
|  | 15950 |  |  | IO&M and PD documents for steam meters, including test reports | Meter data sheets
Vibration Isolation
| Meters & Gauges |  |  |  | IO&M and PD documents
| Access Doors |  |  |  | IO&M and PD documents | As-built location drawings for all access panels and doors
| Exterior Insulation for Ductwork |  |  |  | Care & maintenance instructions
| Pumps and Pumping Systems | 15500 | Min. 8 hours | YES | IO&M and PD documents for HVAC base-mounted pumps and motors | Motor data, performance curves for various impeller sizes and pump speeds |  | Spare parts list
| Air Handling Units | 15500, 15850 | YES | YES | IO&M and PD documents for AHUs, fans, coils, drives, humidifiers, filters, and control valves
| Energy Recovery Equipment | 15850 | YES | YES | IO&M and PD documents for ERUs, enthalpy wheels, etc.
| Variable Frequency Drives | 15500 | YES | YES | IO&M and PD documents, including motor data
| Fan Coil Units | 15750 | YES | YES | IO&M and PD documents
| Humidifiers | 15750 |  |  | IO&M and PD documents
| Unit Heaters |  |  |  | IO&M and PD documents
| Variable Air Volume Boxes |  | Min. 8 hours | YES | IO&M and PD documents
| Fans | 15850 | YES | YES | IO&M and PD documents
| Central Lab Exhaust Fans | 11600, 15850 | YES | YES | IO&M and PD documents
| Laboratory Fume Hoods | 11600 | YES | YES | IO&M and PD documents
| Hydronic Specialties |  |  |  | IO&M and PD documents
| Ductwork Accessories |  |  |  | IO&M and PD documents
| Grilles, Registers, and Diffusers |  |  |  | IO&M and PD documents
| Boilers | 15550 | Min. 24 hours | YES | IO&M and PD documents for boilers and all components (including safety valves) | Manufacturer's data report and NBBPV inspection & certification documents
| Chillers | 15680 | YES | YES | IO&M and PD documents for chillers, plus purge manual, starter manual, variable speed drive manual, and disconnect manual
| Cooling Towers | 15680 | YES | YES | IO&M and PD documents for cooling towers
| Air Terminal Units | 15850, 15950 |  |  | IO&M and PD documents
| Filters |  |  |  | IO&M and PD documents |  | One complete set of filters, all types
| Duct Silencers/Attentuators |  |  |  | IO&M and PD documents
| Dampers | 15850 |  |  | IO&M and PD documents for smoke dampers, fire dampers, and combination smoke/fire dampers
| Louvers |  |  |  | IO&M and PD documents
| Roof Mounted Air Intakes and Vents |  |  |  | IO&M and PD documents
| Building Automation System | 15950 | Min. 32 hours | YES | IO&M and PD documents for water, air, and steam flow measuring stations | As-built sequence(s) of operation
[5 empty] | IO&M and PD documents for pneumatic system air compressors and air dryers | BAS as-builts
[5 empty] | IO&M and PD documents for electronic sensors, thermostates, transmitters, control valves, actuators, detectors, switches, and dampers | Complete control points list, control drawings, and Bill of Materials
[5 empty] | IO&M and PD documents for FACS/DDC control panels | Software Backup: Archive copies of all accepted versions of source code and compiled code for all application programs and data files. All control software must be readily accessible by Owner using BAS server hardware and software. Software file naming for ASC controllers shall match unique ID reference on mechanical drawings. - Copy of the SCT database for the NAE or NCE - CCT (caf file) for the FEC controllers - HVAC Pro or DX-9100 files (if applicable)
| Plumbing Fixtures & Equipment | 15400 |  |  | IO&M and PD documents for water closets, urinals, lavatories, and faucets
|  | 15400 |  |  | IO&M and PD documents for domestic hot water heaters
|  | 15400 |  |  | IO&M and PD documents for domestic water pumps, bladder tanks, and associated controllers
|  | 15400 | YES | YES | IO&M and PD documents for acid dilution or neutralization pits/systems
IO&M and PD documents for water coolers and fountains
|  |  | YES | YES | IO&M and PD documents for solar water heating systems
| Fire protection system | 15300 |  |  | IO&M and PD documents for fire water BFPs | BFP certificates
|  | 15300 |  |  | IO&M and PD documents for FP system pumps
|  | 15300 |  |  | IO&M and PD documents for FP system valves
|  | 15300 | Min. 4 hours | YES | IO&M and PD documents for wet or dry pipe sprinkler systems | "As-built" drawings and hydraulic calculations if design modified
16 | Manholes | 02600 |  |  | IO&M and PD documents for electrical manholes
| Underground Cable | 16300 |  |  | O&M documents for underground cabling, including high-pot test reports
| Generators | 16400, 16600 | Min. 4 hours | YES | IO&M and PD documents for generators, including fuel tanks, pumps, valves, Automatic Transfer Switches, test data/reports, and an itemization of the systems and equipment served by the generator
| Automatic Transfer Switches | 16600 |  |  | IO&M and PD documents
| Load Interrupter Switches |  |  |  | IO&M and PD documents
| Uninterruptable Power Supply System | 16600 | YES | YES | IO&M and PD documents for uninterruptable power systems, including an itemization of the systems and equipment served by the generator
| Transformers | 16300 |  |  | IO&M and PD documents for transformers, including test data/reports
| Switchgear | 16300, 16400 | YES | YES | IO&M and PD documents for switchgear, including switches, alarms, motors, operators, and special features
| Meters & Gauges | 16400 |  |  | IO&M and PD documents for electric meters and current transformers, including test reports | Meter data sheets
| Basic electric materials | 16050 |  |  | PD documents for conductors, conduit, switches, panelboards, breakers
| Electric motors | 16480 |  |  | IO&M and PD documents | Efficiency data for energy rebate
| Interior Lighting | 16500 |  |  | IO&M and PD documents for interior light fixtures/lamps, including emergency/exit lights and exit signs | Floor plans or other means of illustrating access to remote ballasts
| Low Voltage Lighting Control System |  | Min. 4 hours | YES | IO&M and PD documents for lighting control systems and components, including sensors, switches, and programmable "head end" | "As-built" drawings
| Exterior Lighting | 16500 |  |  | IO&M and PD documents for exterior lighting poles, fixtures, lamps, timers, and photocells
| Lighting Protection System |  |  |  | IO&M and PD documents | UL Master Label
| Switches and Circuit Breakers |  |  |  | IO&M and PD documents
| Controllers |  |  |  | IO&M and PD documents
| Panelboards |  |  |  | IO&M and PD documents
| Fire Alarm System | 16723 | YES | YES | IO&M and PD documents for systems and all devices, including pull stations, horn/strobe devices, interface & relay devices, main + annunciator panels | Test data/reports, point-to-point wiring diagrams, a zone map of the building showing the physical location of the devices and the layout of the fire alarm zones, "as-built" control algorithms, and programming guides
| Fire/Smoke Detection System | 16723 | YES | YES | IO&M and PD documents for fire or smoke detection systems and all devices | Test data/reports, point-to-point wiring diagrams, a zone map of the building showing the physical location of the devices and zones, "as-built" control algorithms, and programming guides
17 | Security Systems | 13700 | YES | YES | IO&M and PD documents for security, surveillance, and access control systems | "As-built" wiring diagrams
| Telecomm - Structured Cabling System | CNS/Healthnet |  |  | IO&M and PD documents | Cable test reports and "as-built" drawings
| Telecomm - Other | CNS/Healthnet |  |  | IO&M and PD documents
| CATV/Co-ax | CNS/Healthnet |  |  | IO&M and PD documents
| Audio/Visual Systems |  | YES | YES | IO&M and PD documents | "As-built" drawings and source code
| Assisted Listening Systems | 16752 | YES |  | IO&M and PD documents
18 | Process Systems |  | YES | YES | IO&M and PD documents | "As-built" P&ID drawings